## Scenarios
Jones Family Solar System Calculator
Assume batteries used for all power and only charged by PVs
2020-09-19
Inputs | Scenario |  | A | B | C | D | E
| Architecture |  | 48V DC coupled | 48V DC coupled | 48V DC coupled | 48V DC coupled | 600V PV, 48V battery, 240V AC coupled
| Loads covered with grid |  | All | All except air and water heat | All except air and water heat | All except air and water heat | All except air and water heat
| Days of energy storage | days of energy storage | 1 | 1 | 1 | 0.3 | 0.3
| Types of components |  | premium: LG and Outback Power | premium: LG and Outback Power | premium: LG and Outback Power | premium: LG and Outback Power | premium: LG, SMA and Outback Power
| Annual energy loads to offset, kWh | Air heat | 4300 | 0 | 0 | 0 | 0
|  | Long range EV | 3143 | 3143 | 3143 | 3143 | 3143
|  | Other home uses | 2177 | 2177 | 2177 | 2177 | 2177
|  | Short range EV | 1818 | 1818 | 1818 | 1818 | 1818
|  | Clothes dryer | 822 | 822 | 822 | 822 | 822
|  | Water heat | 660 | 0 | 0 | 0 | 0
|  | Refrigerator | 601 | 601 | 601 | 601 | 601
|  | Lighting | 400 | 400 | 400 | 400 | 400
| Energy bill savings | annual without solar | 1500 | 1000 | 1000 | 1000 | 1000
|  | amount covered by solar system | 100% | 100% | 100% | 100% | 100%
| Inverter/chargers | model | Outback Power Radian GS8048A-01 (plus 2 FM80s and electrical) | Outback Power Radian GS8048A-01 (plus 2 FM80s and electrical) | Outback Power Radian GS8048A-01 (plus 2 FM80s and electrical) | Outback Power Radian GS8048A-01 (plus 2 FM80s and electrical) | ($1,920, 10 year warranty) Battery to and from grid with off grid 240VAC mode: Outback Power Radian GS4048A-01 ($5,515, 5 year warranty)
|  | link | https://www.wholesalesolar.com/1440336/wholesale-solar/power-centers/outback-radian-gs8048a-01-8-000-watt-with-2-fm80-s-inverters-electrical | https://www.wholesalesolar.com/1440336/wholesale-solar/power-centers/outback-radian-gs8048a-01-8-000-watt-with-2-fm80-s-inverters-electrical | https://www.wholesalesolar.com/1440336/wholesale-solar/power-centers/outback-radian-gs8048a-01-8-000-watt-with-2-fm80-s-inverters-electrical | https://www.wholesalesolar.com/1440336/wholesale-solar/power-centers/outback-radian-gs8048a-01-8-000-watt-with-2-fm80-s-inverters-electrical | https://www.wholesalesolar.com/1440325/wholesale-solar/power-centers/outback-radian-4048a-4-000-watt-w-no-controller-inverters-electrical
|  | efficiency | 93% | 93% | 93% | 93% | 93%
|  | cost per inverter/charger | 8780 | 8780 | 8780 | 8780 | 5515
|  | quantity | 1 | 1 | 1 | 1 | 1
|  | warranty, years | 5 | 5 | 5 | 5 | 5
| Inverters (AC coupled only) | model |  |  |  |  | SMA Sunny Boy 7.7-US-41
|  | link |  |  |  |  | https://www.wholesalesolar.com/2931740/sma/solar-inverters-electrical/sma-sunny-boy-7.7-us-41-inverter
|  | efficiency |  |  |  |  | 97%
|  | cost per inverter |  |  |  |  | 1920
|  | quantity |  |  |  |  | 1
|  | warranty, years |  |  |  |  | 10
| Batteries | model | Discover Battery AES 7.4kWhr | Discover Battery AES 7.4kWhr | Discover Battery AES 7.4kWhr | Discover Battery AES 7.4kWhr | Discover Battery AES 7.4kWhr
|  | link | https://www.wholesalesolar.com/9979990/discover/batteries/discover-battery-aes-7.4kwhr-48vdc-with-xanbus-lithium-lfp-battery | https://www.wholesalesolar.com/9979990/discover/batteries/discover-battery-aes-7.4kwhr-48vdc-with-xanbus-lithium-lfp-battery | https://www.wholesalesolar.com/9979990/discover/batteries/discover-battery-aes-7.4kwhr-48vdc-with-xanbus-lithium-lfp-battery | https://www.wholesalesolar.com/9979990/discover/batteries/discover-battery-aes-7.4kwhr-48vdc-with-xanbus-lithium-lfp-battery | https://www.wholesalesolar.com/9979990/discover/batteries/discover-battery-aes-7.4kwhr-48vdc-with-xanbus-lithium-lfp-battery
|  | nameplate capacity, kWh | 7.4 | 7.4 | 7.4 | 7.4 | 7.4
|  | round trip efficiency | 95% | 95% | 95% | 95% | 95%
|  | cost per battery | 6479 | 6479 | 6479 | 6479 | 6479
|  | warranty, years | 10 | 10 | 10 | 10 | 10
|  | maximum depth of discharge | 80% | 80% | 80% | 80% | 80%
|  | capacity at end of warranty period | 80% | 80% | 80% | 80% | 80%
|  | existing battery capacity to be used, kWh - 32 Hipower HP-LFP100AH | 0 | 0 | 10.24 | 10.24 | 10.24
| Charge controllers (DC coupled only) | model | Outback Power FM80 | Outback Power FM80 | Outback Power FM80 | Outback Power FM80
|  | link | https://www.wholesalesolar.com/3510605/outback-power/charge-controllers/outback-power-flexmax-fm80-charge-controller | https://www.wholesalesolar.com/3510605/outback-power/charge-controllers/outback-power-flexmax-fm80-charge-controller | https://www.wholesalesolar.com/3510605/outback-power/charge-controllers/outback-power-flexmax-fm80-charge-controller | https://www.wholesalesolar.com/3510605/outback-power/charge-controllers/outback-power-flexmax-fm80-charge-controller
|  | efficiency | 98% | 98% | 98% | 98%
|  | cost per controller | 515 | 515 | 515 | 515
|  | additional quantity over inverter/charger bundle | 1 | 1 | 1 | 1
|  | warranty, years | 5 | 5 | 5 | 5
| Solar panels | average full sunlight equivalent per day in Santa Rosa CA, hours | 4.7 | 4.7 | 4.7 | 4.7 | 4.7
|  | model | LG NeON2 LG-335N1K-V5 | LG NeON2 LG-335N1K-V5 | LG NeON2 LG-335N1K-V5 | LG NeON2 LG-335N1K-V5 | LG NeON2 LG-335N1K-V5
|  | link | https://www.wholesalesolar.com/1524631/lg/solar-panels/lg-neon2-lg-335n1k-v5-black-black-mono-solar-panel | https://www.wholesalesolar.com/1524631/lg/solar-panels/lg-neon2-lg-335n1k-v5-black-black-mono-solar-panel | https://www.wholesalesolar.com/1524631/lg/solar-panels/lg-neon2-lg-335n1k-v5-black-black-mono-solar-panel | https://www.wholesalesolar.com/1524631/lg/solar-panels/lg-neon2-lg-335n1k-v5-black-black-mono-solar-panel | https://www.wholesalesolar.com/1524631/lg/solar-panels/lg-neon2-lg-335n1k-v5-black-black-mono-solar-panel
|  | peak power, Watts | 330 | 330 | 330 | 330 | 330
|  | cost per panel | 380 | 380 | 380 | 380 | 380
|  | length, inches | 66.38 | 66.38 | 66.38 | 66.38 | 66.38
|  | width, inches | 40 | 40 | 40 | 40 | 40
|  | warranty, years | 25 | 25 | 25 | 25 | 25
|  | capacity at end of warranty period | 80% | 80% | 80% | 80% | 80%
|  | existing solar panel peak power to be used, kW - 12 2003 Sharp NT-180U1s | 0 | 0 | 1.8662 | 1.8662 | 1.8662
| Additional electrical | models | n/a | n/a | n/a | n/a | n/a
|  | links | n/a | n/a | n/a | n/a | n/a
|  | cost | 0 | 0 | 0 | 0 | 0
|  | warranty, years | 5 | 5 | 5 | 5 | 5
Calculations | Average energy required, kWh | in to loads, per year | 13921 | 8961 | 8961 | 8961 | 8961
|  | in to loads, per day | 38.1397 | 24.5507 | 24.5507 | 24.5507 | 24.5507
| Common calculations | in to inverter/charger from batteries, per day | 41.0105 | 26.3986 | 26.3986 | 26.3986 | 26.3986
|  | in to batteries, per day | 43.1689 | 27.788 | 27.788 | 27.788 | 27.788
| DC coupled calculations | in to charge controllers, per day | 44.0499 | 28.3551 | 28.3551 | 28.3551
| AC coupled calculations | in to inverter, per day |  |  |  |  | 28.6474
| Batteries | nameplate capacity required, kWh | 64.0788 | 41.2478 | 41.2478 | 12.3743 | 12.3743
|  | new battery capacity required, kWh | 64.0788 | 41.2478 | 31.0078 | 2.1343 | 2.1343
|  | number of new batteries to buy | 9 | 6 | 4 | 0 | 0
| Solar panels | peak power required, kW | 8.81 | 5.671 | 5.671 | 5.671 | 5.7295
|  | new peak power required, kW | 8.81 | 5.671 | 3.8048 | 3.8048 | 3.8632
|  | number of new panels required | 33.75 | 21.25 | 15 | 15 | 15
| Cost | inverters/chargers | 8780 | 8780 | 8780 | 8780 | 5515
|  | inverters | 0 | 0 | 0 | 0 | 1920
|  | batteries | 58311 | 38874 | 25916 | 0 | 0
|  | charge controllers | 515 | 515 | 515 | 515 | 0
|  | solar panels | 12825 | 8075 | 5700 | 5700 | 5700
|  | additional electrical | 0 | 0 | 0 | 0 | 0
|  | total | 80431 | 56244 | 40911 | 14995 | 13135
| Annual amortization, while existing components last | inverters/chargers | 1756 | 1756 | 1756 | 1756 | 1103
|  | inverters |  |  |  |  | 192
|  | batteries | 5831.1 | 3887.4 | 2591.6 | 0 | 0
|  | charge controllers | 103 | 103 | 103 | 103
|  | solar panels | 513 | 323 | 228 | 228 | 228
|  | additional electrical | 0 | 0 | 0 | 0 | 0
|  | energy bill savings | -1500 | -1000 | -1000 | -1000 | -1000
|  | total | 6703.1 | 5069.4 | 3678.6 | 1087 | 523
| Daily amortization, while existing components last |  | 18.3647 | 13.8888 | 10.0784 | 2.9781 | 1.4329

## energy use data
energy use data, Wh
Air heat | 4300
Long range EV | 3143
Other home uses | 2177
Short range EV | 1818
Clothes dryer | 822
Water heat | 660
Refrigerator | 601
Lighting | 400

## PV panel comparison
PV Panel Comparison | [6 empty] | sorted by:
warranty
Brand | Wattage | cells | price | $/watt | performance | workmanship | $/Watt/year | HQ | Factories
Panasonic | 325 | 60 | 355 | 1.0923 | 25 | 25 | 0.043692 | Japan | Malaysia, US
LG | 360 | 60 | 418 | 1.1611 | 25 | 25 | 0.046444 | South Korea | South Korea, US
Panasonic | 330 | 60 | 390 | 1.1818 | 25 | 25 | 0.047273 | Japan | Malaysia, US
Canadian Solar | 325 | 60 | 209 | 0.64308 | 25 | 12 | 0.05359 | Canada | Canada, China
Heliene | 320 | 60 | 256 | 0.8 | 25 | 10 | 0.08 | Canada | US
Mission Solar | 385 | 72 | 319 | 0.82857 | 25 | 10 | 0.082857 | US | US